## Cover
- | Threat and Risk Analysis Report
JSON-derived workbook in Siemens-style layout
Overview
Field | Value
System | MiniCPS Secure Water Treatment Testbed
Version | MiniCPS SWaT TRA V0 (reference) (0.1)
Status | Under Review
Responsible Organization | Thesis Evaluation Case Study
Created | 2024-11-01
Changed | 2025-01-15
Threat Scenarios | 13
Assets | 9
Protection Goals | 11
Security Zones | 6
Components | 13
Target of Analysis
Six-stage water treatment process control system based on the open-source MiniCPS simulation of the Secure Water Treatment (SWaT) testbed, comprising six stage controllers (PLC1-PLC6), a supervisory SCADA/HMI workstation, a process historian, an engineering workstation, and Level-0 field devices (sensors and actuators) communicating over Modbus-TCP and EtherNet/IP.

## Doc. Details
1 | Document Details
Field | Value
JSON Version | 2
TRA Version Name | MiniCPS SWaT TRA V0 (reference)
TRA Version Number | 0.1
Document Status | Under Review
Created By | Master Thesis Evaluation
Changed By | Master Thesis Evaluation
Created Date | 2024-11-01
Changed Date | 2025-01-15
Project Name | MiniCPS Secure Water Treatment Testbed
Project ID | minicps-swat-v0
Organizational Unit | Thesis Evaluation Case Study
Project Type | Industrial Control System
Access Scope | Public Reference
Config Selection | Software

## Intro
1.1 | Introduction
Purpose
This workbook is a JSON-only Excel rendering of MiniCPS SWaT TRA V0 (reference) for MiniCPS Secure Water Treatment Testbed. Every populated section is derived directly from the source TRA JSON without carrying over unrelated template sample content.
Source Summary
Field | Value
Input File | minicps_swat_tra.json
Threat Scenarios | 13
Assets | 9
Protection Goals | 11
Assumptions | 4
Security Zones | 6
Components | 13

## Attackers
2 | Attacker Types
Type | Threat IDs | Count | Example Threat
Network attacker | T-1; T-2; T-4; T-6; T-10; T-11; T-12; T-13 | 8 | False sensor data injection to PLC1
Internal / authenticated user | T-3; T-5; T-7; T-8; T-9 | 5 | Unauthorised modification of PLC control logic

## Likelihood
3 | Likelihood Scales
Exposure ratings
Rating | Count
Medium | 11
Low | 2
Exploitability ratings
Rating | Count
Medium | 7
Low | 6
Calculated likelihood ratings
Rating | Count
Possible | 9
Unlikely | 3
Likely | 1

## Impact
4 | Impact Scale
PG ID | Type | Impact Level | Impact Category | Description
I-1 | Integrity | Critical | Safety | If sensor readings are forged, controllers act on a false view of the process and can drive the plant into unsafe or out-of-specification states.
I-2 | Integrity | Critical | Safety | Tampered valve or pump commands let an attacker directly drive equipment into damaging or unsafe operation.
I-3 | Integrity | Critical | Process | Modified controller logic can corrupt the entire stage's behaviour persistently, surviving operator intervention.
A-1 | Availability | Critical | Operational | Loss of process control halts water production and may force a plant shutdown.
A-2 | Availability | Moderate | Operational | If supervisory monitoring is lost, operators are blind to process state and cannot respond to developing problems.
I-4 | Integrity | Moderate | Forensic | Falsified historian records can hide an ongoing attack and undermine incident investigation.
I-5 | Integrity | Moderate | Operational | A tampered HMI can mask alarms and present a false picture of the plant to operators.
I-6 | Integrity | Critical | Process | Corrupted project sources propagate malicious logic to controllers on the next download.
C-1 | Confidentiality | Moderate | Intellectual Property | Disclosure of setpoints and control logic helps an attacker craft a precise, stealthy process manipulation.
A-3 | Availability | Critical | Safety | Coordinated manipulation of sensors and actuators can cause tank overflow or chemical overdosing with safety and environmental consequences.
C-2 | Confidentiality | Negligible | Operational | The aggregated production statistics in the historian are of low sensitivity and disclosure has minimal consequence.

## Risk
5 | Risk and Risk Matrix
Risk Rating | Threat Count | Threat IDs
Moderate | 13 | T-1; T-2; T-3; T-4; T-5; T-6; T-7; T-8; T-9; T-10; T-11; T-12; T-13

## System Overview
6 | System Overview
Scope of TRA
Six-stage water treatment process control system based on the open-source MiniCPS simulation of the Secure Water Treatment (SWaT) testbed, comprising six stage controllers (PLC1-PLC6), a supervisory SCADA/HMI workstation, a process historian, an engineering workstation, and Level-0 field devices (sensors and actuators) communicating over Modbus-TCP and EtherNet/IP.
Components
Component | Scope | Security Zone | Description
PLC1 - Raw Water Supply | In Scope | SZ-3 | Stage 1 controller managing raw water intake, the inlet motorised valve MV101 and the raw water pump P101 based on tank level transmitter LIT101.
PLC2 - Chemical Dosing | In Scope | SZ-3 | Stage 2 controller managing pre-treatment chemical dosing pumps and the analyser instruments AIT201-AIT203 for pH, ORP and conductivity.
PLC3 - Ultrafiltration | In Scope | SZ-3 | Stage 3 controller managing the ultrafiltration feed pump and backwash sequencing.
PLC4 - Dechlorination | In Scope | SZ-3 | Stage 4 controller managing UV dechlorination and sodium-bisulphite dosing before reverse osmosis.
PLC5 - Reverse Osmosis | In Scope | SZ-3 | Stage 5 controller managing the high-pressure reverse-osmosis pumps and permeate quality monitoring.
PLC6 - Permeate and Backwash | In Scope | SZ-3 | Stage 6 controller managing permeate transfer to product storage, membrane backwash and chemical cleaning.
SCADA / HMI Workstation | In Scope | SZ-2 | Supervisory workstation presenting live process state and alarms to operators and forwarding operator commands to the controllers.
Process Historian | In Scope | SZ-2 | Server collecting and retaining the time-series record of process variables, alarms and operator actions for monitoring and forensics.
Engineering Workstation | In Scope | SZ-5 | Maintenance host used by control engineers to develop, compile and download controller logic to PLC1-PLC6.
Level-0 Field Devices | In Scope | SZ-4 | The aggregate of Stage-1 to Stage-6 sensors and actuators (level transmitters, flow meters, analysers, motorised valves and pumps) wired to their stage controllers.
Plant Firewall | Out of Scope | SZ-1 | Boundary firewall between the supervisory network and the enterprise network; treated as part of the environment rather than analysed in depth.
Vendor Remote Support | Out of Scope | SZ-6 | Occasional vendor remote-support access from an external network; excluded because it is governed by a separate access agreement and is out of the analysis boundary.
Enterprise Reporting Client | Out of Scope | SZ-1 | Business reporting client on the enterprise network that reads aggregated production data; excluded as it only consumes already-published reports.

## Int. Op. Env.
7 | Intended Operational Environment
Operational Environment
The system continuously controls a six-stage water purification process: raw water intake and storage (Stage 1), chemical pre-treatment and dosing (Stage 2), ultrafiltration (Stage 3), dechlorination by UV and sodium bisulphite (Stage 4), reverse osmosis (Stage 5), and permeate transfer, backwash and cleaning (Stage 6). Each stage is governed by a dedicated programmable logic controller (PLC1-PLC6) that reads level, flow and quality sensors and drives motorised valves and pumps. The PLCs exchange process state over a Level-1 control ring network and report to a Level-2 supervisory network hosting the SCADA/HMI workstation and the process historian. Operators monitor and command the plant through the HMI; engineers maintain controller logic from an engineering workstation. The plant is expected to run unattended for long periods, with operators intervening only on alarms.
Intended Users
Plant operators, control engineers, and maintenance staff of the water treatment facility.
Assumptions
ID | Name | Validated | Zone IDs | Description
A_zone-1 | Field wiring physically protected | Yes | SZ-4 | Level-0 sensor and actuator wiring runs inside locked control cabinets and conduit within the physically secured plant floor, so direct physical tampering with field signals requires defeating site access controls first.
A_zone-2 | Engineering workstation hardened | Yes | SZ-5 | The engineering workstation is a managed host with application allow-listing, current operating-system patches, and disabled removable-media autorun, and it is only used for controller maintenance tasks.
A_zone-3 | Plant boundary firewall segmentation | No | SZ-1 | A firewall is expected to separate the Level-2 supervisory network from the enterprise and external networks, but the rule set has not yet been audited and the segmentation is therefore not yet confirmed.
A_zone-4 | Control protocols lack authentication | Yes | SZ-3 | The Modbus-TCP and EtherNet/IP protocols used on the Level-1 control ring provide no message authentication or integrity protection, so any host on the control network can read and write process data.

## Prot. Goals
8 | Protection Goals
PG ID | Name | Type | Impact | Asset | Threat IDs | Description
I-1 | Integrity of sensor measurements | Integrity | Critical | Data-1 | T-1 | If sensor readings are forged, controllers act on a false view of the process and can drive the plant into unsafe or out-of-specification states.
I-2 | Integrity of actuator commands | Integrity | Critical | Data-3 | T-2 | Tampered valve or pump commands let an attacker directly drive equipment into damaging or unsafe operation.
I-3 | Integrity of PLC control logic | Integrity | Critical | Data-2 | T-3; T-9 | Modified controller logic can corrupt the entire stage's behaviour persistently, surviving operator intervention.
A-1 | Availability of water treatment process | Availability | Critical | Func-1 | T-4; T-6; T-13 | Loss of process control halts water production and may force a plant shutdown.
A-2 | Availability of SCADA monitoring | Availability | Moderate | Func-3 | T-5 | If supervisory monitoring is lost, operators are blind to process state and cannot respond to developing problems.
I-4 | Integrity of historian data | Integrity | Moderate | Data-4 | T-7 | Falsified historian records can hide an ongoing attack and undermine incident investigation.
I-5 | Integrity of HMI configuration | Integrity | Moderate | Data-5 | T-8 | A tampered HMI can mask alarms and present a false picture of the plant to operators.
I-6 | Integrity of engineering project files | Integrity | Critical | Data-6 | T-9 | Corrupted project sources propagate malicious logic to controllers on the next download.
C-1 | Confidentiality of process design and setpoints | Confidentiality | Moderate | Data-2 | T-10 | Disclosure of setpoints and control logic helps an attacker craft a precise, stealthy process manipulation.
A-3 | Physical plant and process safety | Availability | Critical | Func-2 | T-11; T-12 | Coordinated manipulation of sensors and actuators can cause tank overflow or chemical overdosing with safety and environmental consequences.
C-2 | Confidentiality of historian reporting data | Confidentiality | Negligible | Data-4 |  | The aggregated production statistics in the historian are of low sensitivity and disclosure has minimal consequence.

## Assets
9 | Asset Description
Asset ID | Name | Type | Description | Protection Goals | Threat IDs
Data-1 | Sensor measurements | Data | Level, flow, pH, ORP and conductivity readings reported by Level-0 field instruments to the stage controllers. | I-1 | T-1
Data-2 | PLC control logic and setpoints | Data | The ladder/structured-text control programs and process setpoints executing on PLC1-PLC6 that determine valve and pump behaviour. | I-3; C-1 | T-10; T-3; T-9
Data-3 | Actuator command signals | Data | Open/close and start/stop commands issued by the controllers to motorised valves and pumps. | I-2 | T-2
Data-4 | Historian process database | Data | The time-series record of process variables, alarms and operator actions retained for monitoring, reporting and forensic analysis. | I-4; C-2 | T-7
Data-5 | HMI configuration and views | Data | The graphics, tag mappings and alarm definitions presented to operators on the SCADA/HMI workstation. | I-5 | T-8
Data-6 | Engineering project files | Data | The controller project sources and download images managed on the engineering workstation. | I-6 | T-9
Func-1 | Water treatment process operation | Functionality | The continuous availability of the six-stage purification process producing water that meets quality targets. | A-1 | T-13; T-4; T-6
Func-2 | Physical plant safety | Functionality | The prevention of unsafe physical states such as tank overflow, dry-running pumps, and chemical overdosing. | A-3 | T-11; T-12
Func-3 | SCADA monitoring functionality | Functionality | The operators' ability to observe live process state and receive alarms through the supervisory system. | A-2 | T-5

## Threat&Risk List
10 | Threat and Risk List
Threat ID | Component/Asset | Threat Description | PG | Attacker Type | Weakness / Problem | Exposure | Exploitability | Impact | Likelihood | Risk | Mitigation | Acceptance Comment | Attack Interface | Threat Name
T-1 | PLC1 - Raw Water Supply | An attacker on the Level-1 control network spoofs Modbus responses so that PLC1 receives a forged low level reading from LIT101, causing the controller to keep the inlet valve open and overfill the raw water tank. | I-1 | Network attacker | Unauthenticated Modbus-TCP allows a control-network host to forge sensor responses. | Medium | Medium | Critical | Possible | Moderate | Deploy control-network monitoring and physical high-level overflow interlocks independent of PLC1. | High risk is not accepted by default and requires the listed mitigation. | LI-1 | False sensor data injection to PLC1
T-2 | PLC1 - Raw Water Supply | An attacker performing a man-in-the-middle on the control ring rewrites Modbus write requests so that motorised valve MV101 is commanded open against the controller's intent, driving the actuator into an unsafe position. | I-2 | Network attacker | No integrity protection on Modbus write commands permits in-flight tampering. | Medium | Medium | Critical | Possible | Moderate | Segment the control ring and apply unidirectional or authenticated command channels where feasible. | Residual high risk requires mitigation before acceptance. | LI-1 | Actuator command manipulation on control ring
T-3 | Engineering Workstation | An attacker who reaches the engineering download interface downloads altered control logic to a stage controller, persistently changing how the stage responds to process conditions. | I-3 | Internal / authenticated user | Controller program download is not cryptographically authenticated or signed. | Low | Low | Critical | Unlikely | Moderate | Enforce controller key-switch run/program protection and signed project downloads. | Critical risk is explicitly not accepted and tracked for treatment. | LI-9 | Unauthorised modification of PLC control logic
T-4 | PLC3 - Ultrafiltration | An attacker floods the Level-1 control ring with traffic so that controllers can no longer exchange process state with the supervisory system, causing loss of coordinated process control. | A-1 | Network attacker | The control ring has limited bandwidth and no traffic prioritisation against flooding. | Medium | Medium | Moderate | Possible | Moderate |  | Moderate risk accepted by default with monitoring. | LI-3 | Denial of service on the control ring
T-5 | SCADA / HMI Workstation | An attacker exploits a vulnerability on the supervisory workstation to disrupt the HMI service, so operators lose their live view of the process and cannot react to alarms. | A-2 | Internal / authenticated user | The supervisory workstation runs general-purpose software with a broad attack surface. | Medium | Medium | Moderate | Possible | Moderate |  | Moderate risk accepted by default with workstation hardening. | LI-7 | Compromise of the SCADA/HMI workstation
T-6 | PLC2 - Chemical Dosing | An attacker on the control network injects a forged command that stops pump P101, interrupting raw water supply to the downstream stages and disrupting production. | A-1 | Network attacker | Unauthenticated control protocol accepts any well-formed command from the network. | Medium | Medium | Moderate | Likely | Moderate | Add command-source filtering and anomaly detection on the control network. | High risk requires the listed mitigation. | LI-2 | Spoofed stop command halts raw water pump
T-7 | Process Historian | An attacker who reaches the historian query API alters stored process records to erase the evidence of a manipulation, undermining later incident investigation. | I-4 | Internal / authenticated user | Historian records lack tamper-evident storage or write segregation. | Medium | Low | Moderate | Unlikely | Moderate |  | Low risk accepted by default. | LI-8 | Tampering with historian records
T-8 | SCADA / HMI Workstation | An attacker modifies the HMI configuration so that critical alarms are suppressed or recoloured, leaving operators unaware that the process has entered an abnormal state. | I-5 | Internal / authenticated user | HMI configuration can be changed without independent alarm verification. | Medium | Low | Moderate | Possible | Moderate |  | Moderate risk accepted by default with configuration change control. | LI-7 | HMI alarm masking
T-9 | Engineering Workstation | An attacker plants malware on the engineering workstation that injects malicious logic into the controller project files, so the next legitimate download propagates the manipulation to a stage controller. | I-3; I-6 | Internal / authenticated user | Project files are not integrity-verified before download to the controller. | Low | Low | Critical | Unlikely | Moderate | Apply project-file signing, workstation EDR, and removable-media controls. | Critical supply-chain-style risk is not accepted by default. | LI-9 | Malware on engineering workstation alters controller project
T-10 | PLC5 - Reverse Osmosis | An attacker passively captures unencrypted Modbus traffic on the control network to learn the reverse-osmosis setpoints and control logic needed to craft a stealthy future manipulation. | C-1 | Network attacker | Modbus-TCP transmits process data and setpoints in clear text. | Medium | Medium | Moderate | Possible | Moderate |  | Low confidentiality risk accepted by default for this process. | LI-5 | Eavesdropping on unencrypted control traffic
T-11 | PLC1 - Raw Water Supply | An attacker simultaneously spoofs the LIT101 level reading and forces the inlet valve open through PLC1, defeating the controller's level protection and driving the raw water tank to physical overflow. | A-3 | Network attacker | A single compromised control path governs both the level reading and the inlet actuator without independent interlock. | Medium | Low | Critical | Possible | Moderate | Install a hardwired independent high-level switch that closes the inlet regardless of PLC1 state. | Critical safety risk is not accepted and requires an independent protection layer. | LI-1 | Coordinated overflow of the raw water tank
T-12 | PLC2 - Chemical Dosing | An attacker forces PLC2 to run the chemical dosing pumps beyond their safe setpoint, overdosing the water with treatment chemicals and producing an out-of-specification, potentially hazardous product stream. | A-3 | Network attacker | Dosing setpoints can be overridden over the unauthenticated control interface. | Medium | Low | Critical | Possible | Moderate | Enforce physical dosing-rate limiters and independent quality analysers with shutdown interlocks. | Critical safety risk requires independent dosing limits. | LI-2 | Chemical overdose via dosing controller manipulation
T-13 | PLC4 - Dechlorination | An attacker captures and replays earlier EtherNet/IP command frames to PLC4 so that a stale dechlorination setting is reapplied at the wrong time, degrading downstream reverse-osmosis protection. | A-1 | Network attacker | EtherNet/IP frames carry no freshness or sequence protection against replay. | Medium | Medium | Moderate | Possible | Moderate |  | Moderate risk accepted by default with network monitoring. | LI-4 | Replay attack on dechlorination controller

## Reporting
11 | Reporting
Risk distribution
Risk | Count | Threat IDs
Moderate | 13 | T-1; T-2; T-3; T-4; T-5; T-6; T-7; T-8; T-9; T-10; T-11; T-12; T-13
Impact distribution
Impact | Count
Critical | 6
Moderate | 7

## Internal
12 | Internal Cross References
Type | ID | Name | Linked IDs
SecurityZone | SZ-1 | Plant Enterprise Network (Level 3)
SecurityZone | SZ-2 | Supervisory Network (Level 2)
SecurityZone | SZ-3 | Control Network (Level 1)
SecurityZone | SZ-4 | Field Network (Level 0)
SecurityZone | SZ-5 | Engineering Zone
SecurityZone | SZ-6 | External / Internet
Component | SW-1 | PLC1 - Raw Water Supply | LI-1
Component | SW-2 | PLC2 - Chemical Dosing | LI-2
Component | SW-3 | PLC3 - Ultrafiltration | LI-3
Component | SW-4 | PLC4 - Dechlorination | LI-4
Component | SW-5 | PLC5 - Reverse Osmosis | LI-5
Component | SW-6 | PLC6 - Permeate and Backwash | LI-6
Component | SW-7 | SCADA / HMI Workstation | LI-7
Component | SW-8 | Process Historian | LI-8
Component | SW-9 | Engineering Workstation | LI-9
Component | SW-10 | Level-0 Field Devices | LI-10
Component | SW-11 | Plant Firewall
Component | SW-12 | Vendor Remote Support
Component | SW-13 | Enterprise Reporting Client